Welcome
 Connecting batteries in parallel
Unexpected effects and solutions
Battery Power Conference
Sept. 18 2012
Davide Andrea, Elithion

---
Elithion
Lithium-ion BMS for large batteries
Traction packs
Battery modules for large arrays

---
Overview
- Paralleling at the factory vs. in the field
- Parallel cells, not strings
- Introducing “Short Discharge Time”
- Issues with paralleling batteries in the field
- Some solutions for those issues

---
Factory vs field
At the factory:
Parelleled once and for all
Reason
To get desired capacity
In the field:
Paralleled at any old time
Reason
For flexibility

---
Cell in parallel vs. strings in parallel
(at the factory)
Cells in parallel	Strings in parallel
Cellis in parallel, then sets in series / (lattice network)	Cells in series, then strings in parallel

---
Cell in parallel vs. strings in parallel
BMS cell boards or tap points
Cells in parallel	Strings in parallel
4 cell boards, or 5 tap points	16 cell boards, or 14 tap points

---
Cell in parallel vs. strings in parallel
Low cell capacity limitation
Cells in parallel	Strings in parallel

---
Cell in parallel vs. strings in parallel
Hi cell resistance limitation
Cells in parallel	Strings in parallel
Bad cell reduces capacity / NO LOAD UNDER LOAD	Bad cell shuts down battery / NO LOAD UNDER LOAD

---
Strings in parallel
One switch vs many switches
One switch per string	String directly in parallel
Bad string can be isolated	Bad cell shuts down battery

---
Parallel connection in the field
Reasons:
- To carry only required capacity
- To add to depleted battery
- To service a battery
- To add redundancy
Issues:
- Inrush current with differing SOC
- Keeping track of SOC, capacity

---
Parallel connection in the field
The fuel tank mindset: you can always add fuel tanks to increase range.
This is not applicable to batteries.

---
The fuel tank analogy
One tank at a time
Bad analogy to batteries in parallel

---
Adding a full battery
when the first battery is empty
Charge rushes into the empty battery: heat!

---
Initial connection (in field)
Batteries as voltage sources
Batteries are voltage sources:
Series: easy
Parallel: problematic
If ideal voltage sources...
= ∞A
Parallel ideal voltage sources = infinite current
V1 - V2
0 Ω

---
Initial connection (in field)
Way to parallel voltage sources
Ideally, voltage sources are connected through current sources
Or, at least, through resistors
Never directly

---
Initial connection (in field)
Real world batteries
Resistance is non-0
Voltage changes with SOC
Vb1 - Vb2
R1 + R2
i(t) =

---
Initial connection (in field)
Damage from inrush current
- Damage to interconnects
- Damage to cells? Possible if:
  - High dV/dSOC (standard Li-ion)
  - Low Rseries

---
Short discharge time
Definition
- Theoretical discharge time across a short circuit
- Constant, characteristic of each cell technology, regardless of capacity or voltage
- Easy calculation of resistance
  - R = TShortDisch * Voltage / Capacity
Easy calculation of efficiency
  - Eheat = Eout * TShortDisch / TActualDisch
Ranges from ~10 s to ~250 s

---
Short discharge time
for various cell families
NiCd
NiMH
Adv LA
Lead acid

---
Specific Power vs.
Short discharge time
Specific power	Short discharge time
Marketing more than engineering? / Achievable in reality	Mathematically precise / Not achievable in reality

---
Short discharge time
Short discharge time vs energy density

---
Initial connection (in field)
Worst case
- EIG F007 cells (LiPo, 7 Ah, 1.6 mΩ)
  - Lowest resistance, high dV/dSOC
- N-1 cells 100 % SOC + 1 cell 0 % SOC
EMPTY
CELL
FULL
CELLS
- (4.2 V – 2.7 V) / 1.6 mΩ = 940 A-pk = 134 C-pk
  - In general 4 ~ 134 C peak

---
Initial connection (in field)
2 cells
- KOKAM SLPB....H5 cells (LiPo, 5 Ah, 3 mΩ)
- 1 cell 100 % SOC + 1 cell 0 % SOC2
2 kWh
wasted

---
Initial connection (in field)
Energy and charge loss
Charge loss	Energy loss
No charge is lost: / Just as many electrons flow out of the most charged battery as flow into the least charged one.	A bit of energy is lost: / The current through the connecting resistance produces heat. / The energy loss is: / ~12 % for std Li-ion / ~8 % for LiFePO4 / Less for delta SOC < 100 % / Independent of resistance

---
Paralleling batteries
Factory vs. field
Paralleling at the factory: OK
Cells all have same SOC
Paralleling in the field: not ideal
Possible damage with low resistance cells
BMS's SOC value may become invalid
BMS may be off, or current could exceed BMS's range
Energy loss ~10 % @ ΔSOC = 100 %

---
Paralleling techniques (in field)
To minimize inrush
- Wait for equal voltages, or
- Charge lowest battery, or
- Discharge highest battery, or
- Transfer energy between batteries (DC-DC)
  THEN you can connect in parallel

---
Paralleling techniques (in field)
SOC and capacity evaluation
Each battery requires its own BMS (& SOC)
SOC after connection:
High inrush: each BMS estimates SOC from OCV
Low inrush: each BMS calcs SOC from current
Master BMS computes SOC and capacity of entire pack from individual battery SOCs

---
Conclusions
At the factory
- Paralleling at the factory is OK
  - Parallel cells directly (not strings)

---
Conclusions
In the field
- Paralleling in the field can be a problem
  - Avoid if possible:
    - Damage, loss of energy, complex calculations
  - But, if you must:
    - Use 1 BMS & 1 switch / string
    - Prevent high inrush at connection by equalizing voltages before connecting
    - Calculate capacity and pack SOC from each battery's capacity and SOC

---
Thank you
Questions?